## Slide 1: Time-Domain Protection Scheme for Microgrids with Aggregated Inverter-Based Distributed Energy Resources
Husam Samkari, PhD, PE
Assistant Professor
University of Tabuk
July 26, 2024

## Slide 2: Outline
Introduction
  Objective
  Problem Definition
Background
  Protection Challenges
  Superimposed Quantities
Proposed Protection Scheme
  Radial Systems
  Communication
Proposed Relay
  Time-Domain and Phasor-Based Protection
  Operating Characteristic
  Trip Logic
EMTP Model
Key Results
  Fault Types and Location
  Grid-Isolated and Interconnected Modes
Conclusions

## Slide 3: Introduction: Microgrids
Localized power systems
  Distributed energy resources (DER)
  Energy storage system (ESS)
Disconnect and connect to bulk power system (BPS)
  Grid-Isolated mode
  Grid-Interconnected mode
Operate autonomously
Strengthening power grid resilience

## Slide 4: Introduction: Problem Definition
Protecting microgrid systems
  Wide variation in fault current levels (two operation modes)
  Dynamic changes in microgrid topology and generation availability
  Bidirectional power flow in feeders
Integrating IBRs into microgrid systems
  Unique fault current characteristics
  Fast control response
  No inherent inertia

## Slide 5: Introduction: Research Objective
Develop protection scheme and relay that functions:
  In microgrids with inverter-based resources (IBRs)
  During grid-interconnected and grid-isolated modes
  In systems with radial, loop, and dynamic topologies
  With fast tripping scheme to retain stability for severe faults
Reference [1], [2], and [3]

## Slide 6: Background: Microgrids Protection Challenges
(a) During grid-interconnected, fault current supplied by BPS and distributed energy resources (DER)
(b) During grid-isolated, fault current supplied by DER
(c) During grid-interconnected, but DER disconnected, fault current supplied by BPS

## Slide 7: Background: IBRs Fault Current Characteristics
Low fault current magnitudes around 1.2 per unit
Nonlinear behavior relative to fault location and fault type
High-frequency transient for first ¼ of power cycle
Primarily dependent on IBRs control and independent of fault location
Predominantly positive-sequence

## Slide 8: Background: Time-Domain Superimposed
Superimposed (also know as incremental) quantities
  Fault-generated components
  Zero when no changes presents
  Indicate fault direction using transient power
Δ𝑆(𝑡) = (Δ𝑣𝑎(𝑡) Δ𝑖𝑎(𝑡) + Δ𝑣𝑏(𝑡) Δ𝑖𝑏(𝑡) + Δ𝑣𝑐(𝑡) Δ𝑖𝑐(𝑡))
  Forward = Negative
  Reverse = Positive
Reference [3]

## Slide 9: Background: Replica Impedance Filter
Why?
  Eliminate dc offset from propagating to current quantities (conventional source)
  Useful for reflecting true transient power direction
Replica impedance filter
  Scaled by source impedance behind relay
  User setting depending on the power system
  High-pass filter that functions as mimic filter
Δ𝑖𝑟𝑝(𝑡) = (𝑅𝑠/|𝑍𝑠|) ∗ Δ𝑖(𝑡) + (𝐿𝑠 / |𝑍𝑠|) ∗ 𝑑/𝑑𝑡 (Δ𝑖(𝑡))
Reference [3]

## Slide 10: Background: IBR Compared to Other Resources
Single line to ground
Fault supplied by the IBR
  Not reliable signals
  Because of IBR fast response
Wind type-1 and synchronous generator
  Reliable replica power signal
  dc offset removed
Reference [3]

## Slide 11: Proposed Protection Scheme
Low bandwidth communication between relays
Modified directional comparison scheme
  Radial, loop and dynamic microgrid topologies
In-Zone fault:
  One relay at boarder of zone declares forward (FWD)
  The other relay declares reverse (REV)
Out-of-Zone fault:
  Both relays declare FWD or REV
Reference [2]

## Slide 12: Proposed Protection Scheme: Radial Systems
Reference is microgrid’s point of common coupling (PCC)
Downstream looking from PCC to end of feeder (FWD)
Upstream looking back to PCC (REV)
Reference [2]

## Slide 13: Proposed Relay
Reference [2]

## Slide 14: Proposed Relay: Time-Domain Protection
Digital quantities processed through per-phase delta filters
Applies decoupled double synchronous reference frame (DDSRF) algorithm
  Improve signals’ reliability
  Calculate instantaneous symmetrical components
Reference [2]

## Slide 15: Proposed Relay: Phasor-Based Protection
Symmetrical components transformation is applied to phasor three-phase voltage components
Delta filter is applied to calculate superimposed voltage
  Used to restrain the overcurrent element
Reference [2]

## Slide 16: Proposed Relay: Operating Characteristic
Output from DDSRF
  Superimposed positive-sequence direct-axis current
  Superimposed positive-sequence direct-axis voltage
Calculate instantaneous power "Watt component”
Calculate instantaneous energy

## Slide 17: Proposed Relay: Trip Logic
From the Time-Domain Protection
Reference [2]

## Slide 18: EMTP Model
IBR aggregated model: 2 MW
  Three phase two-level VSC
  IBR Control
  Photovoltaic (PV) model
Superimposed relay model
  Time-Domain
  Phasor-Based
  Communication
  Logic

## Slide 19: Study Case
Impact of IBR [3]
Generic microgrid system [2]
Transmission line with sending and receiving ends [1]
IEEE 34-bus system
  Unbalanced three-phase radial system
  Actual feeder that was in Arizona
  Nominal voltage of 24.9 kV
  Unbalanced loading

## Slide 20: Study Case: Modified IEEE 34-Bus
Reference [2]

## Slide 21: Results: Comparing the Proposed Method
Watt component (ΔWd1) reliable when IBR is the main source of fault current
Proposed method reduces IBRs impact
ΔWd1

## Slide 22: Results: SLG Fault, Grid-Isolated, Location 1
Single line to ground fault
Grid-Isolated Mode
(a) Relay at node 846
  Fault supplied by conventional source
(b) Relay at node 848
  Fault supplied by IBR
Direction of fault in 2.6 ms
IN-ZONE asserted in 6.6 ms
TRIP asserted in 7.7 ms

## Slide 23: Results: DLG Fault, Grid-Isolated, Location 2
Double line to ground fault
Grid-Isolated Mode
(a) Relay at node 816
  Fault supplied by conventional source
(b) Relay at node 824
  Fault supplied by IBR
Direction of fault in 2.2 ms
IN-ZONE asserted in 6.1 ms
TRIP asserted in 6.9 ms

## Slide 24: Results: LL Fault, Grid-Interconnected, Location 3
Line to line fault
Grid-Interconnected Mode
(a) Relay at node 858
  Fault supplied by conventional source
(b) Relay at node 834
  Fault supplied by IBR
Direction of fault in 2.4 ms
IN-ZONE asserted in 6.4 ms
TRIP asserted in 6.7 ms

## Slide 25: Results: Signals Response Time Statistics
Statistics for 120 tests
  10 possibilities of fault types
  Low and high Rf
  3 locations and both modes
Average response time
  FWD/REV < ¼ cycle
  IN-ZONE < ½ cycle
  TRIP ≈ ½ cycle
Maximum response time
  FWD/REV < ½ cycle
  IN-ZONE < 1 cycle
  TRIP ≈ 1 cycle
Reference [2]

## Slide 26: Conclusions
Proposed relays trip for in-zone fault in half-cycle
  Requiring only low bandwidth communication
  During grid-interconnected and grid-isolated modes
The average response time to indicate fault direction is 3 ms and to identify fault zone is 7 ms
The proposed relay provides reliable directional element when IBR is the main source of fault current
  DDSRF used to calculate superimposed positive-sequence direct energy

## Slide 27: Conclusions (continued)
Proposed scheme and relay functioned reliably based on study cases conducted
However, very high fault resistance conditions in stiff systems are challenging
  Because scheme sensitivity determined by voltage threshold
DDSRF introduces 1 ms delay to superimposed quantities

## Slide 28: Future Work
To put this scheme to practical use:
  More testing is required including evaluation for different types and sizes of microgrids
  Test DDSRF-based superimposed element using hardware-in-the-loop simulation and physical test environments
  Model systems with large numbers of IBRs instead of aggregated IBRs
  Conducting more sensitivity analysis on proposed relay

## Slide 29: THANK YOU!
Contact Information:
Husam Samkari, PhD, PE
hsamkari@ut.edu.sa

## Slide 30: References
Samkari, H.S.; Johnson, B.K., "Superimposed Quantities-Based Protection for Transmission Lines with Inverter-Based Resources,“ IEEE PES General Meeting, 2024
Samkari, H.S.; Johnson, B.K., "Time-Domain Protection Scheme for Microgrids with Aggregated Inverter-Based Distributed Energy Resources,“ IEEE Access, 2023
Samkari, H.S.; Johnson, B.K., "Impact of Distributed Inverter-Based Resources on Incremental Quantities-Based Protection,“ IEEE PES General Meeting, 2021